Technical Information sheet

ASHP Installation Notes

   Installation Notes
- At the main enclosure terminate the Cat 5 cable using an RJ45 plug (according to the 586B convention) and patch into the appropriate port in the patch panel
- All ports are labeled on the diagram in the main enclosure
- Link 1: At the ASHP use the blue and blue white core of the Cat 5 and connect these to the volt free link terminals, which are used to toggle heating demand
- Link 2: At the ASHP use the green and green white core of the Cat 5 and connect this to the volt free link terminals, which are used to toggle cooling demand
- The 230v alarm output of the ASHP has to be connected to the appropriate relay (terminal A2) in the main enclosure
- Connect the second terminal on the relay (terminal A1) to neutral on the ASHP circuit
- All relays are labeled on the diagram in the main enclosure
NOTE: Both line (alarm output) and neutral have to come from the ASHP to prevent mixing the neutrals

Technical Notes

The ASHP is powered on its own circuit and only control signals are provided from the main enclosure..

The ASHP has two volt free link interfaces which can be used to indicate heating or cooling demand.

If Link 1 is closed then this indicates a heating demand. If Link 1 and Link 2 are closed then this indicates a cooling demand.

On the WebBrick the volt free links are made or broken using one of the WebBrick's internal relays.

Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com
  Installation Diagram

  Intelligent Building Automation