Technical Information sheet

Boiler Installation Notes

 Installation Notes
- At the main enclosure terminate the Cat 5 cable using an RJ45 plug (according to the 586B convention) and patch into the appropriate port in the patch panel
- All ports are labeled on the diagram in the main enclosure
- At the boiler use only the blue and blue white core of the Cat 5 and connect these to the volt free link terminal, which are used to toggle demand
- The 230v alarm output of the boiler has to be connected to the appropriate relay (terminal A2) in the main enclosure
- Connect the second terminal on the relay (terminal A1) to neutral on the boiler circuit
- All relays are labeled on the diagram in the main enclosure
NOTE: Both line (alarm output) and neutral have to come from the boiler to prevent mixing the neutrals

Technical Notes

The boiler is powered on its own circuit and only control signals are provided from the main enclosure.

The boiler has a volt free link interface which can be used to indicate demand.

On the WebBrick the volt free link is made or broken using one of the WebBrick's internal relays.

For Support contact:

01635 897 301

or email: info@webbricksystems.com

Intelligent Building Automation

 Installation Diagram

  Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com