Technical Information sheet

Energy Meter Installation Notes

   Installation Notes
- At the main enclosure terminate the Cat 5 cable using an RJ45 plug (according to the 586B convention) and patch into the appropriate socket in the patch panel
- All ports are labeled on the diagram in the main enclosure
- If the energy meter is using the same Cat 5 cable as the ASHP, then use the orange and orange white core of the Cat 5. The orange and white core is terminated at terminal 8 and the orange core is terminated at terminal 9
- If the energy meter is using its own Cat 5 cable, then use the blue and blue white core of the Cat 5. The blue and white core is terminated at terminal 8 and the blue core is terminated at terminal 9

Technical Notes

The energy meter is powered on its own circuit and only monitoring signals are taken back to the main enclosure.

On the WebBrick the energy meter is connected to the digital input.

  Installation Diagram

  Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com