Technical Information sheet

Fan Coil Unit Installation Notes

   Installation Notes
- Two Cat 5 cables are used for control and monitoring of the fan coil unit
- At the zone hub terminate the Cat 5 cable using an RJ45 plug (according to the 586B convention) and patch into the appropriate port in the patch panel
- All ports are labeled on the diagram in the zone hub
- At the fan coil unit the temperature sensor Cat 5 is punched down into the ICD connector using the 586B colour scheme
- At the fan coil unit the other Cat 5 cable (fan speed control) is terminated as follows:
  - all white cores are connected to 'G'
  - the blue core is connected to channel 1
  - the green core is connected to channel 2
  - the orange core is connected to channel 3
  - the brown core is connected to channel 4

Technical Notes

The fan coil unit is powered on its own circuit and only control signals are provided from the zone hub.

Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com
  Installation Diagram

  Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com