Technical Information sheet

Motorised Valve Installation Notes

 Installation Notes

- Connect the neutral (blue) of the valve to one of the bussed neutral connections in the main enclosure
- Then connect the line drive open and the line drive close to the correct numbered terminals in the main enclosure

NOTE: Do NOT terminate the neutral of the motorised valve anywhere but the main enclosure to prevent mixing the neutrals!

- At the main enclosure terminate the Cat 5 cable using an RJ45 plug (according to the 586B convention) and patch into the appropriate port in the patch panel
- All ports are labeled on the diagram in the main enclosure
At the motorised valve use only the blue and blue white core of the Cat 5 and connect these to the position contact on the valve
NOTE: The position contact has to be set to make the link (create a contact) when the valve is fully closed
Technical Notes

The motorised valves are powered directly from the main enclosure.

Motorised valves have 3 connections (neutral (blue), line to drive open (usually brown), line to drive closed (usually black).

Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com

  Installation Diagram

  Intelligent Building Automation

For Support contact:

01635 897 301

or email: info@webbricksystems.com